## Slide 1
MODULE 03
Traps & Vents
Why traps fail, how vents protect them, and the venting methods every Texas plumber must know cold.
TX Plumbing Exam Coach · Educational use only

## Slide 2
TRAPS
How a P-trap actually works
Inlet → dip → weir → outlet — the bend holds a water seal.
Seal depth: 2" minimum, 4" maximum (deep-seal traps allowed).
Loss of seal causes: siphonage, back-pressure, evaporation, capillary action, wind effect.
Trap arm: from trap weir to the vent fitting.
03 · Traps & Vents
2 / 8

## Slide 3
TRAP RULES
Memorize these limits
2–4"
TRAP SEAL
Min/max liquid seal depth.
24"
FROM FIX.
Max vertical distance, fixture outlet to trap weir.
1
TRAP
One trap per fixture — no double trapping.
03 · Traps & Vents
3 / 8

## Slide 4
VENTS
Common venting methods
Individual / Common
Individual vent — serves one trap.
Common vent — two traps at the same level on a shared drain.
Most reliable, easiest to inspect.
Wet / Circuit / Island
Wet vent — drain doubles as vent for upstream fixtures.
Circuit vent — battery of fixtures vented through one branch vent.
Island vent — loop vent for sinks with no nearby wall.
03 · Traps & Vents
4 / 8

## Slide 5
SLOPE
Horizontal drain slope (typical)
2½" and smaller: ¼ inch per foot minimum.
3" to 6": ⅛ inch per foot minimum.
8" and larger: 1/16 inch per foot minimum.
Too steep can be as bad as too flat — solids drop, water races ahead.
03 · Traps & Vents
5 / 8

## Slide 6
FAILURE MODES
Why traps lose their seal
Self-siphonage — fixture discharge pulls its own seal out (vent fixes this).
Back-pressure — surge below pushes seal up and out.
Evaporation — floor drains in unused spaces; use trap primers.
Capillary — string/lint draped over weir wicks water away.
Wind effect — gusts across an unvented vent terminal.
03 · Traps & Vents
6 / 8

## Slide 7
CHECK
Knowledge Check
Maximum vertical distance from a fixture outlet to the trap weir?
A. 12 inches
B. 18 inches
C. 24 inches
D. 30 inches
Answer: C — Codes cap this at 24" to keep the seal stable.
03 · Traps & Vents
7 / 8

## Slide 8
Keep flowing.
03 · Traps & Vents
Review · Drill · Pass. TX Plumbing Exam Coach
Educational and exam-prep use only. Not an official TSBPE product or legal substitute for adopted plumbing codes.