## Slide 1
MODULE 04
Fuel Gas Fundamentals
Sizing natural gas and LP systems, reading load tables, and passing the pressure test the first time.
TX Plumbing Exam Coach · Educational use only

## Slide 2
BASICS
Two fuels, one code
Natural gas — ~1,000 BTU/cu ft, lighter than air (rises on leak).
LP (propane) — ~2,500 BTU/cu ft, heavier than air (settles low).
Both governed by the IFGC plus local amendments.
Convert appliance BTU/hr to CFH: CFH = BTU/hr ÷ heating value.
04 · Fuel Gas
2 / 7

## Slide 3
KEY NUMBERS
Memorize for the exam
1,000
BTU / CF
Natural gas heating value.
2,500
BTU / CF
Propane (LP) heating value.
0.5 psi
STD SUPPLY
Typical residential supply pressure.
04 · Fuel Gas
3 / 7

## Slide 4
SIZING
Pipe-sizing workflow
Steps
List every appliance and its BTU/hr.
Convert to CFH using the heating value.
Measure longest run from meter to farthest appliance.
Use that length for ALL branches (longest-length method).
Pick pipe size from the IFGC table.
Watch for
CSST requires bonding per IFGC 310.
Drip leg at each appliance (where required).
Shutoff within 6 ft of each appliance.
No unions inside concealed spaces.
04 · Fuel Gas
4 / 7

## Slide 5
PRESSURE TEST
Standard residential air test
Isolate from meter and appliances.
Pressurize to at least 3 psi (or 1.5× working, not less than 3 psi).
Hold for the time required by the AHJ — typically 15 min minimum.
No drop on the gauge = pass. Any drop = locate and repair.
04 · Fuel Gas
5 / 7

## Slide 6
CHECK
Knowledge Check
A 100,000 BTU/hr furnace on natural gas requires roughly how many CFH?
A. 10 CFH
B. 40 CFH
C. 100 CFH
D. 1,000 CFH
Answer: C — 100,000 ÷ 1,000 BTU/cf ≈ 100 CFH.
04 · Fuel Gas
6 / 7

## Slide 7
Keep flowing.
04 · Fuel Gas
Review · Drill · Pass. TX Plumbing Exam Coach
Educational and exam-prep use only. Not an official TSBPE product or legal substitute for adopted plumbing codes.